## Slide 1: Estimating loss coefficient for baffled flocculators
Hypothesis: every right angle change in direction causes streamlines to compress to approximately 60% (Cc).
Thus after two direction changes the flow is compressed to Cc2b.
Flow expands at a rate somewhat greater than 1:10 and reattaches to the baffle before a distance of 10(1-Cc2)b
b
V
Ccb
Cc2b

## Slide 2: Contraction → Expansion → Head Loss
Notes: Schulz and Okun say K varies between 2.5 and 4.

## Slide 3: Questions that need answers
How far should the baffle extend?
Could they be made much shorter and still get the desired mixing?
Add crossbars to get more mixing?
Plan view
Elevation view

## Slide 4: How can we estimate wall shear?
What is the maximum wall shear?
Calculate a minimum value by assuming a linear velocity gradient
We need a better description of the velocity gradient
b
V
Ccb
Cc2b

## Slide 5: How could we improve Hydraulic Flocculator Design?
Where is the velocity gradient lowest and how could the velocity gradient be increased there?
Flocculator Design Project (120 L/min) research plant to be installed at the CUWTP